## Version
Version | Date | Author | Description
2.0 | 2023-06-01 | jmlegrand@smartd.co | Inital draft of version v2 * Added version and profile registers * Updated links to update automatically
2.1 | 2023-09-12 | jmlegrand@smartd.co | * Added registers to expose temperatures and fans count (not implemented yet) * Added documentation of Device Info code 43 request/responses (not implemented yet)
2.2 | 2023-09-26 | jmlegrand@smartd.co | * Added registers for torque (not implemented yet) * Added motor nameplate (not implemented yet) * Added I/Os state registers (not implemented yet) * Added motor controller metrics (not implemented yet)
2.3 | 2023-12-12 | dmacrae@smartd.co | * Added PID

## Instructions
SmartDrive - Communication Parameters
EXPLANATORY NOTE: This Excel file is for reference only. Refer to the Clean Power VFD
user guide, section about communication, for full information.
The columns include the following criteria:
Code:
Language-independent, this allows a rapid search in the programming manual, which
includes an index of parameter codes.
Profile:
Profile name.
Holding address:
Addresses for Modbus Holding Register
Address for the messaging are in hexadecimal (preceded by 16#) format.
To optimize messaging performance, addresses are given for the control word (MCx) and
the status word (SYSx).
The addresses annotated "speed" are for use in rpm; the addresses annotated "frequency"
are for use in Hz.
Link:
For control word and system word a link is given to their description.
Access:
Read and write options:
R: Read only
W: Write only
R/W: Write, then read
Type:
WORD (Enumeration)
FLAGS (Unsigned)
IEEE754: 32-bit floating point
Unsigned32
Units:
Physical units.
Factory Setting:
Value of the parameter set at the factory.
Range:
Possible values.
Description:
Indicates a description.
Reference:
Gives to the SmartDrive variables document.

## Device Info (code43)
Request for basic information
| Definition |  | Number of Bytes | Value | Comment
| Slave number |  | 1 | 0xFF | ?
| Function code |  | 1 | 0x2B
| Sub-function code |  | 1 | 0x0E
| Product ID |  | 1 | 0x01
| Object Identifier |  | 1 | 0x00
Response for basic information
| Definition |  | Number of Bytes | Value | Comment
| Slave number |  | 1 | 0xFF | ?
| Function code |  | 1 | 0x2B
| Sub-function code |  | 1 | 0x0E
| Product ID |  | 1 | 0x01
| Conformity level |  | 1 | 0x01
| Reserved |  | 1 | 0x00
| Reserved |  | 1 | 0x00
| Number of objects |  | 1 | 0x03
| Object 0: manufactorer name | Object number | 1 | 0x00
|  | Object length | 1 | 0x18
|  | Object content | 24 | SmartD Technologies Inc.
| Object 1: product code | Object number | 1 | 0x01
|  | Object length | 1 | 0x0A (min) | Product code is having variable length.
|  | Object content | 10 (min) | Examples: SDB-1-2185 SDB-1-2185-A | Product code is having variable length.
| Object 2: version number | Object number | 1 | 0x02
|  | Object length | 1 | 0x0B
|  | Object content | 19 | Vxxxx.yy.zz | Example: V2023.11.00
Request for complete information
| Definition |  | Number of Bytes | Value | Comment
| Slave number |  | 1 | 0xFF | ?
| Function code |  | 1 | 0x2B
| Sub-function code |  | 1 | 0x0E
| Product ID |  | 1 | 0x02
| Object Identifier |  | 1 | 0x00
Response for complete information
| Definition |  | Number of Bytes | Value | Comment
| Slave number |  | 1 | 0xFF | ?
| Function code |  | 1 | 0x2B
| Sub-function code |  | 1 | 0x0E
| Product ID |  | 1 | 0x01
| Conformity level |  | 1 | 0x02
| Reserved |  | 1 | 0x00
| Reserved |  | 1 | 0x00
| Number of objects |  | 1 | 0x05
| Object 0: manufactorer name | Object number | 1 | 0x00
|  | Object length | 1 | 0x18
|  | Object content | 24 | SmartD Technologies Inc.
| Object 1: product code | Object number | 1 | 0x01
|  | Object length | 1 | 0x0A (min) | Product code is having variable length.
|  | Object content | 10 (min) | Examples: SDB-1-2185 SDB-1-2185-A | Product code is having variable length.
| Object 2: version number | Object number | 1 | 0x02
|  | Object length | 1 | 0x0B
|  | Object content | 19 | Vxxxx.yy.zz | Example: V2023.11.00
| Object 3: manufacturer URL | Object number | 1 | 0x03
|  | Object length | 1 | 0x13
|  | Object content | 19 | https://smartd.tech
| Object 4: product name | Object number | 1 | 0x04
|  | Object length | 1 | 0x0F
|  | Object content | 15 | Clean Power VFD

## Parameters
Code | Service | Name | Holding address | IEC61800-7-201 Object | IEC61800-7-201 Name | IEC61800-7-201 Category | Link | Access | Type | Units | Factory setting | Range | Multiplier Factor | Description | Reference
| SmartD Power Meter | OperationalData.line.L1_current | 16#0000 |  |  |  |  | R | Unsigned16 | A |  | 0.00 ... (depends on drive model) | 100 | Current measured on L1 input line | SmartDrive Variables - power_meter
| SmartD Power Meter | OperationalData.line.L2_current | 16#0001 |  |  |  |  | R | Unsigned16 | A |  | 0.00 ... (depends on drive model) | 100 | Current measured on L2 input line | SmartDrive Variables - power_meter
| SmartD Power Meter | OperationalData.line.L3_current | 16#0002 |  |  |  |  | R | Unsigned16 | A |  | 0.00 ... (depends on drive model) | 100 | Current measured on L3 input line | SmartDrive Variables - power_meter
| SmartD Power Meter | OperationalData.line.L12_voltage | 16#0003 |  |  |  |  | R | Unsigned16 | Vrms |  | 0.00 ... (depends on drive model) | 10 | Voltage between input lines 1 and 2 | SmartDrive Variables - power_meter
| SmartD Power Meter | OperationalData.line.L23_voltage | 16#0004 |  |  |  |  | R | Unsigned16 | Vrms |  | 0.00 ... (depends on drive model) | 10 | Voltage between input lines 2 and 3 | SmartDrive Variables - power_meter
| SmartD Power Meter | OperationalData.line.L31_voltage | 16#0005 |  |  |  |  | R | Unsigned16 | Vrms |  | 0.00 ... (depends on drive model) | 10 | Voltage between input lines 1 and 3 | SmartDrive Variables - power_meter
| SmartD Power Meter | OperationalData.line.frequency | 16#0006 |  |  |  |  | R | Unsigned16 | Hz |  | 0.00 ... 100.00 | 100 | Frequency of the signal measured on the input lines L1/L2/L3. | SmartDrive Variables - power_meter
| SmartD Power Meter | OperationalData.line.real_power | 16#0007 |  |  |  |  | R | Signed16 | Watts |  | 0.00 ... 100,000.00 | 0.01 | The actual amount of power being used, or dissipated by the drive and the motor attached to the drive. | SmartDrive Variables - power_meter
| SmartD Power Meter | OperationalData.line.apparent_power | 16#0008 |  |  |  |  | R | Signed16 | VA |  | 0.00 ... 100,000.00 | 0.01 | Apparent power is the power the grid must be able to withstand at the current moment to power the drive and the motor controlled by this drive. | SmartDrive Variables - power_meter
| SmartD Power Meter | OperationalData.line.reactive_power | 16#0009 |  |  |  |  | R | Signed16 | VAR |  | -100,000.00 ... 100,0000.00 | 0.01 | Reactive power represents electrical energy stored in the drive coils and motor that then flows back to the grid. | SmartDrive Variables - power_meter
| SmartD Power Meter | OperationalData.line.power_factor | 16#000A |  |  |  |  | R | Signed16 |  |  | -1.00 ... 1.00 | 100 | The power factor is defined as the ratio of the real power absorbed by the drive and its load to the apparent power flowing in the drive. | SmartDrive Variables - power_meter
| SmartD Power Meter | OperationalData.motor.U_current | 16#0100 |  |  |  |  | R | Unsigned16 | A |  | 0.00 ... (depends on drive model) | 100 | Current measured on U output line | SmartDrive Variables - power_meter
| SmartD Power Meter | OperationalData.motor.V_current | 16#0101 |  |  |  |  | R | Unsigned16 | A |  | 0.00 ... (depends on drive model) | 100 | Current measured on V output line | SmartDrive Variables - power_meter
| SmartD Power Meter | OperationalData.motor.W_current | 16#0102 |  |  |  |  | R | Unsigned16 | A |  | 0.00 ... (depends on drive model) | 100 | Current measured on W output line | SmartDrive Variables - power_meter
| SmartD Power Meter | OperationalData.motor.UV_voltage | 16#0103 |  |  |  |  | R | Unsigned16 | Vrms |  | 0.00 ... (depends on drive model) | 10 | Voltage between output lines U and V | SmartDrive Variables - power_meter
| SmartD Power Meter | OperationalData.motor.VW_voltage | 16#0104 |  |  |  |  | R | Unsigned16 | Vrms |  | 0.00 ... (depends on drive model) | 10 | Voltage between output lines V and W | SmartDrive Variables - power_meter
| SmartD Power Meter | OperationalData.motor.UW_voltage | 16#0105 |  |  |  |  | R | Unsigned16 | Vrms |  | 0.00 ... (depends on drive model) | 10 | Voltage between output lines U and W | SmartDrive Variables - power_meter
| SmartD Power Meter | OperationalData.motor.frequency | 16#0106 |  |  |  |  | R | Unsigned16 | Hz |  | 0.00 ... 120.00 | 100 | Frequency of signal the outputed on lines U/V/W. | SmartDrive Variables - power_meter
| SmartD Power Meter | OperationalData.motor.balance | 16#0107 |  |  |  |  | R | Unsigned16 | % |  | 0.00 ... 1.00 | 100 | The motor is considered balanced if the voltages, currents and power factors in all three phases are identical. Conversely, when any of these parameters are not identical the circuit is classified as unbalanced. | SmartDrive Variables - power_meter
| SmartD Power Meter | OperationalData.motor.real_power | 16#0108 |  |  |  |  | R | Signed16 | Watts |  | 0.00 ... 100,000.00 | 0.01 | The actual amount of power being used, or dissipated by the motor (and other loads) attached to the drive. | SmartDrive Variables - power_meter
| SmartD Power Meter | OperationalData.motor.apparent_power | 16#0109 |  |  |  |  | R | Signed16 | VA |  | 0.00 ... 100,000.00 | 0.01 | Apparent power is the power the drive must be able to withstand at the current moment to power the motor and other loads controlled by this drive. | SmartDrive Variables - power_meter
| SmartD Power Meter | OperationalData.motor.reactive_power | 16#010A |  |  |  |  | R | Signed16 | VAR |  | -100,000.00 ... 100,000.00 | 0.01 | Reactive power represents electrical energy stored in the drive coils and motor that then flows back to the grid. | SmartDrive Variables - power_meter
| SmartD Power Meter | OperationalData.motor.power_factor | 16#010B |  |  |  |  | R | Signed16 |  |  | -1.00 ... 1.00 | 100 | The power factor is defined as the ratio of the real power absorbed by the drive and its load to the apparent power flowing to motor (and other loads). | SmartDrive Variables - power_meter
| SmartD Power Meter | OperationalData.dcbus.Vdc_plus_voltage | 16#0200 |  |  |  |  | R | Unsigned16 | V |  | 0.00 ... 1,000.00 | 10 | Votlage measure on postive side of the internal DC bus of the drive. | SmartDrive Variables - power_meter
| SmartD Power Meter | OperationalData.dcbus.Vdc_minus_voltage | 16#0201 |  |  |  |  | R | Unsigned16 | V |  | 0.00 ... 1,000.00 | 10 | Votlage measure on postive side of the internal DC bus of the drive. | SmartDrive Variables - power_meter
| SmartD Motor Controller | OperationalData.motor_state | 16#0400 |  |  |  | MCS | R | WORD (Enumeration) |  |  |  |  | State of the motor. | SmartDrive Variables - motor_controller
| SmartD Motor Controller | OperationalData.direction | 16#0401 |  |  |  | MCD | R | WORD (Enumeration) |  |  |  |  | Rotation direction of the shaft. | SmartDrive Variables - motor_controller
| SmartD Motor Controller | OperationalData.frequency | 16#0402 |  |  |  |  | R | Unsigned16 | Hz |  | 0.0 .. 120.0 | 100 | Current motor synchronous speed. | SmartDrive Variables - motor_controller
| SmartD Motor Controller | OperationalData.velocity | 16#0403 |  |  |  |  | R | Unsigned16 | rpm |  | 0 .. 7200 | 1 | Current motor synchronous speed. | SmartDrive Variables - motor_controller
| SmartD Motor Controller | OperationalData.mode | 16#0404 |  |  |  | MCM | R | WORD (Enumeration) |  |  |  |  | Motor operation mode
N/A | SmartD Motor Controller | OperationalData.torque | 16#0405 |  |  |  |  | R | Signed16 | % |  | -250 .. 250 | 100 | Current estimated motor torque
| SmartD Motor Controller | SetPoints.command | 16#0410 |  |  |  | MCC | R/W | WORD (Enumeration) |  |  |  |  | Requested state of the output inverter of the drive. | SmartDrive Variables - motor_controller
| SmartD Motor Controller | SetPoints.direction | 16#0411 |  |  |  | MCD | R/W | WORD (Enumeration) |  |  |  |  | Rotation direction of the shaf. | SmartDrive Variables - motor_controller
| SmartD Motor Controller | SetPoints.frequency | 16#0412 |  |  |  |  | R/W | Unsigned16 | Hz |  | 0.0 .. 120.0 | 100 | Desired motor synchronous speed. | SmartDrive Variables - motor_controller
| SmartD Motor Controller | SetPoints.presetFrequency | 16#0413 |  |  |  |  | R/W | Unsigned16 |  |  | 0 .. 7 | 1 | Get or set the preset frequency index | SmartDrive Variables - motor_controller
| SmartD Motor Controller | SetPoints.velocity | 16#0414 |  |  |  |  | R/W | Unsigned16 | rpm |  | 0 .. 7200 | 1 | Desired motor shaft velocity | SmartDrive Variables - motor_controller
| SmartD Motor Controller | SetPoints.presetVelocity | 16#0415 |  |  |  |  | R/W | Unsigned16 |  |  | 0 .. 7 | 1 | Get or set the preset velocity index | SmartDrive Variables - motor_controller
N/A | SmartD Motor Controller | SetPoints.torque | 16#0416 |  |  |  |  | R/W | Signed16 | % |  | -250 .. 250 | 100 | Desired motor torque | SmartDrive Variables - motor_controller
N/A | SmartD Motor Controller | SetPoints.presetTorque | 16#0417 |  |  |  |  | R/W | Unsigned16 |  |  | 0 .. 7 | 1 | Get or set the preset torque index | SmartDrive Variables - motor_controller
| SmartD Motor Controller | SePotins.mode | 16#0418 |  |  |  |  | R/W | WORD (Enumeration)
N/A | SmartD Motor Controller | Configuration.motorNameplate.nominalInputFrequency | 16#0460 |  |  |  |  | R | Unsigned16 | Hz |  | 50 or 60 | 100 | Nominal motor frequency
N/A | SmartD Motor Controller | Configuration.motorNameplate.nominalVelocity | 16#0461 |  |  |  |  | R | Unsigned16 | rpm |  | 0 .. 7200 | 10 | Nominal motor shaft speed
N/A | SmartD Motor Controller | Configuration.motorNameplate.nominalVoltage | 16#0462 |  |  |  |  | R | Unsigned16 | Vrms |  | 0 ... (480 or 600 depends on drive model) | 100 | Nominal motor voltage
N/A | SmartD Motor Controller | Configuration.motorNameplate.nominalCurrent | 16#0463 |  |  |  |  | R | Unsigned16 | A |  | 0 ... (depends on drive model) | 100 | Moninal motor current (FLA)
N/A | SmartD Motor Controller | Configuration.motorNameplate.minInputFrequency | 16#0464 |  |  |  |  | R | Unsigned16 | Hz |  | 0 .. 119 | 100 | Minimum motor frequency
N/A | SmartD Motor Controller | Configuration.motorNameplate.maxInputFrequency | 16#0465 |  |  |  |  | R | Unsigned16 | Hz |  | 1 .. 120 | 100 | Maximum motor frequency
16
N/A | SmartD Motor Controller | Metrics.lifeTime.startCountLowWord | 16#0500 |  |  |  |  | R | Unsigned16 |  | 0 | 0 .. 65535 | 1 | Number of times the VFD has been started (bit 15..0) of a 32-bit counter
N/A | SmartD Motor Controller | Metrics.lifeTime.startCountHighWord | 16#0501 |  |  |  |  | R | Unsigned16 |  | 0 | 0 .. 65535 | 1 | Number of times the VFD has been started (bit 31..16) of a 32-bit counter
N/A | SmartD Motor Controller | Metrics.lifeTime.runTimeLowWord | 16#0502 |  |  |  |  | R | Unsigned16 | seconds | 0 | 0 .. 65535 | 1 | Cumulative VFD runtime (bit 15..0) of a 32-bit counter
N/A | SmartD Motor Controller | Metrics.lifeTime.runTimeHighWord | 16#0503 |  |  |  |  | R | Unsigned16 | seconds | 0 | 0 .. 65535 | 1 | Cumulative VFD has been started (bit 31..16) of a 32-bit counter
N/A | SmartD Motor Controller | Metrics.runTime.startCountLowWord | 16#0504 |  |  |  |  | R | Unsigned16 |  | 0 | 0 .. 65535 | 1 | Number of times the motor has been started (bit 15..0) of a 32-bit counter - could be reset when the user replace the motor
N/A | SmartD Motor Controller | Metrics.runTime.startCountHighWord | 16#0505 |  |  |  |  | R | Unsigned16 |  | 0 | 0 .. 65535 | 1 | Number of times the motor has been started (bit 31..16) of a 32-bit counter - could be reset when the user replace the motor
N/A | SmartD Motor Controller | Metrics.runTime.runTimeLowWord | 16#0506 |  |  |  |  | R | Unsigned16 | seconds | 0 | 0 .. 65535 | 1 | Cumulative motor runtime (bit 15..0) of a 32-bit counter - could be reset when the user replace the motor
N/A | SmartD Motor Controller | Metrics.runTime.runTimeHighWord | 16#0507 |  |  |  |  | R | Unsigned16 | seconds | 0 | 0 .. 65535 | 1 | Cumulative motor has been started (bit 31..16) of a 32-bit counter - could be reset when the user replace the motor
N/A | SmartD Cooling Management | OperationalData.driveTemperature | 16#0600 |  |  |  |  | R | Signed16 | Degree C |  | -20.0 .. 140.0 | 10 | Drive power electronic temperature.
N/A | SmartD Cooling Management | OperationalData.driveAmbiantTemperature | 16#0601 |  |  |  |  | R | Signed16 | Degree C |  | -20.0 .. 140.0 | 10 | Drive internal temperature. Ususaly lower than OperationalData.drive_temperature
N/A | SmartD Cooling Management | OperationalData.fanCount | 16#0602 |  |  |  |  | R | Unsigned16 | rpm |  | 1 .. 4 | 1 | Number of fans available on this
N/A | SmartD Cooling Management | OperationalData.fans[0].speed | 16#0603 |  |  |  |  | R | Unsigned16 | rpm |  | 0 .. 65535 | 1 | Fan#1 speed in RPM
N/A | SmartD Cooling Management | OperationalData.fans[1].speed | 16#0604 |  |  |  |  | R | Unsigned16 | rpm |  | 0 .. 65535 | 1 | Fan#1 speed in RPM
N/A | SmartD Cooling Management | OperationalData.fans[2].speed | 16#0605 |  |  |  |  | R | Unsigned16 | rpm |  | 0 .. 65535 | 1 | Fan#1 speed in RPM
N/A | SmartD Cooling Management | OperationalData.fans[3].speed | 16#0606 |  |  |  |  | R | Unsigned16 | rpm |  | 0 .. 65535 | 1 | Fan#1 speed in RPM
| SmartD System | OperationalData.system_state | 16#0800 |  |  |  | SYS | R | WORD (Enumeration) |  |  |  |  | System state. | SmartDrive Variables - system
| SmartD System | ResetLockout | 16#0840 |  |  |  | SYSR | W | WORD (Enumeration) |  |  |  |  | System state reset. | SmartDrive Variables - system
| SmartD System | ControlModeSetpoints.setControlMode | 16#0900 |  |  |  | SYSRC | R/W | WORD (Enumeration) |  |  |  |  | Select local vs remote control | SmartDrive Variables - motor_controller
| SmartD System | ControlModeSetpoints.setRemoteControlSource | 16#0901 |  |  |  | SYSRCS | R/W | WORD (Enumeration) |  |  | 0 - 2 | 1 | Select remote source 1 or 2, 0 unspecified | SmartDrive Variables - motor_controller
N/A | SmartD I/Os | OperationalData.digitalInputs | 16#0940 |  |  |  | DIS | R | FLAGS (Unsigned16) |  |  |  |  | State of the digital intputs
N/A | SmartD I/Os | OperationalData.relays | 16#0941 |  |  |  | RELAYS | R | FLAGS (Unsigned16) |  |  |  |  | State of the relays
N/A | SmartD I/Os | OperationalData.analogInput1 | 16#0950 |  |  |  |  | R | Unsigned16 | % |  | 0 .. 100%, do we wan't to keep room up 250% | 100 | AI1 value in % relative to min/max values configured for the I/O
N/A | SmartD I/Os | OperationalData.analogInput2 | 16#0951 |  |  |  |  | R | Unsigned16 | % |  | 0 .. 100%, do we wan't to keep room up 250% | 100 | AI2 value in % relative to min/max values configured for the I/O
N/A | SmartD I/Os | OperationalData.analogInput3 | 16#0952 |  |  |  |  | R | Unsigned16 | % |  | 0 .. 100%, do we wan't to keep room up 250% | 100 | AI3 value in % relative to min/max values configured for the I/O
N/A | SmartD I/Os | OperationalData.analogOutput1 | 16#0960 |  |  |  |  | R | Unsigned16 | % |  | 0 .. 100%, do we wan't to keep room up 250% | 100 | AQ1 value in % relative to min/max values configured for the I/O
N/A | SmartD I/Os | OperationalData.analogOutput2 | 16#0961 |  |  |  |  | R | Unsigned16 | % |  | 0 .. 100%, do we wan't to keep room up 250% | 100 | AQ2 value in % relative to min/max values configured for the I/O
| SmartD Alarms | Alarm flags #1 | 16#0C00 |  |  |  | AL1 | R/W | FLAGS (Unsigned16) |  |  |  |  | Read: Arm flags. Write: Alarm acks. | SmartDrive Variables - alarms
| SmartD Alarms | Alarm flags #2 | 16#0C01 |  |  |  | AL2 | R/W | FLAGS (Unsigned16) |  |  |  |  | Read: Arm flags. Write: Alarm acks. | SmartDrive Variables - alarms
| SmartD Alarms | Alarm flags #3 | 16#0C02 |  |  |  | AL3 | R/W | FLAGS (Unsigned16) |  |  |  |  | Read: Arm flags. Write: Alarm acks. | SmartDrive Variables - alarms
| SmartD Alarms | Alarm flags #4 | 16#0C03 |  |  |  | AL4 | R/W | FLAGS (Unsigned16) |  |  |  |  | Read: Arm flags. Write: Alarm acks. | SmartDrive Variables - alarms
| SmartD PID#1 | OperationalData.feedbackValue | 16#0D00 |  |  |  |  | R | Signed16 | % |  | -250 .. 250 (support overshoot) | 100 | Read the process value of PID index 1. % relative to PID1 setpoint range configuration. Values outside range saturate to min/max
| SmartD PID#1 | SetPoints.desiredProcessValue | 16#0D01 |  |  |  |  | R/W | Unsigned16 | % |  | 0.. 100 | 100 | Read/Write the desired process setpoint value of PID index 1. % relative to PID1 setpoint range configuration. Values above maximum saturate to maximum value. Values below minimum throw exception
| SmartD PID#1 | SetPoints.outputMode | 16#0D02 |  |  |  | PIDOM | R/W | Unsigned16 |  |  |  |  | Read/Write PID index 1: Select Output Mode
| SmartD PID#1 | SetPoints.forcedOutputValueFrequency | 16#0D03 |  |  |  |  | R/W | Unsigned16 | Hz |  | 0.0 .. 120.0 | 100 | Read/Write the forced output value in frequecy (Hz)
| SmartD PID#1 | SetPoints.forcedOutputValueVelocity | 16#0D04 |  |  |  |  | R/W | Unsigned16 | rpm |  | 0 .. 7200 | 1 | Read/Write the force output value in velocity (rpm)
| SmartD MODBUS ID | Profile Version | 16#FF00 |  |  |  | MBPV | R | BITFIELD (Unsigned16) |  | 16#0200 |  |  | MODBUS Profile version minor
| Reserved | Reserved | 16#FF01 |  |  |  |  | R | Unsigned16 |  | 16#0000 |  |  | Reserved
| SmartD MODBUS Profile ID | Profile ID | 16#FF02 |  |  |  | MBPID | R | WORD (Enumeration) |  | 16#0000 |  |  | List of profile must be defined lateer.
| SmartD MODBUS Heartbeat | Heartbeat register | 16#FF03 |  |  |  |  | R | Unsigned16 |  | 16#0000 |  |  | This value increment every 1s on the VFD
Legend
Implemented
N/A | Not implemented

## Enumerations
List ID | Value | Display | Description
MCS | 0 | Unspecified
| 1 | Disabled | Motor is halted and command ON is forbidden.
| 2 | Halted | Motor is halted.
| 3 | Ramping Up | Motor is ramping up.
| 4 | Running | Motor is running in steady state.
| 5 | Ramping Down | Motor is ramping down.
| 6 | Autotuning | Motor has autotuning in progress.
| 7 | Paused | Motor is still active, but not turning. Will start turning again on a motor speed change command
MCD | 0 | Unspecified
| 1 | Forward
| 2 | Reverse
MCC | 0 | Unspecified
| 1 | On | Start motor.
| 2 | Off | Stop motor.
| 3 | Enable | Allow ON and OFF commands.
| 4 | Disabled | Disallow ON and OFF commands. If motor is not halted, then OFF command will also be sent.
| 5 | Halt | Sends the motor in freewheeling mode
| 6 | Pause | Pause motor from turning. Will start back on a speed change
SYSRC | 0 | Unspecified | Control mode unspecified
| 1 | Local | Local control mode
| 2 | Remote | Remote control mode
SYSRCS | 0 | Unspecified | Remote source is unspecified
| 1 | Remote Source 1 | Remote source 1
| 2 | Remote Source 2 | Remote source 2
SYS | 0 | Unspecified
| 1 | Booting | The system is booting up.
| 2 | Unconfigured | The system is waiting to be configured. This is the default system state after a factory reset.
| 3 | Ready To Run | The system has gone through the configuration process and is ready to run.
| 4 | Running Auto tuning | The system is auto tuning.
| 5 | Running Normal | The system is running normally and driving a motor.
| 6 | Running Emergency | The system is running in emergency mode. Most alarms are ignored.
| 7 | Running OSS | The system is in maintenance mode.
| 8 | Lockout | The system is in lockout and requires a power cycle to be reset.
| 9 | Shutting Down | The system is shutting down.
| 10 | Factory Reset | The system is applying a factory reset and will shut down after it is done.
| 11 | Fault | The system is in fault but can recover if the active fault(s) get resolved.
SYSR | 0 | No operation
| != 0 | Reset faults | Perform reset lockout.
MBPID | 0 | SmartD
TBD
MCM | 0 | Unspecified | No mode has been set
| 1 | Frequency Mode | Drive is using frequency setpoint
| 2 | Preset frequency Mode | Drive is using preset frequency index setpoints
| 3 | Velocity Mode | Drive is using velocity setpoint
| 4 | Preset Velocity Mode | Drive is using preset velocity setpoint
PFOT | 0 | Unspecified | No type has been set
| 1 | Value | PID using forced output value
| 2 | Preset | PID using forced output preset
PIDOM | 0 | Unspecified | No mode has been set
| 1 | Control Mode | PID is in closed loop control mode (regulating)
| 2 | Forced Output Mode | PID is in Forced Output Mode

## Registers
Bit is written in big-endian
AL1 | Alarm flags: |  | Read: 1 = alarm active, 0 = alarm inactive. Write: 1 = ack alarm, 0 = no operation.
|  | Bit 0 | Unspecified
|  | Bit 1 | STO
|  | Bit 2 | STO Loss
|  | Bit 3 | Line phase inversion
|  | Bit 4 | DC Undervoltage
|  | Bit 5 | DC Overvoltage
|  | Bit 6 | Line voltage sag
|  | Bit 7 | Line voltage balance
|  | Bit 8 | Line phase loss
|  | Bit 9 | HMI Communication Loss
|  | Bit 10 | Line current balance
|  | Bit 11 | Line overcurrent
|  | Bit 12 | Motor current balance
|  | Bit 13 | Motor overcurrent
|  | Bit 14 | Motor overtemp
|  | Bit 15 | Motor Overload
AL2 | Alarm flags: |  | Read: 1 = alarm active, 0 = alarm inactive. Write: 1 = ack alarm, 0 = no operation.
|  | Bit 0 | Drive overtemp
|  | Bit 1 | Unknown boot state
|  | Bit 2 | Booted backup software
|  | Bit 3 | Booted backup software with default config
|  | Bit 4 | Drive high temperature
|  | Bit 5 | Line voltage swell
|  | Bit 6 | Software update failed
|  | Bit 7 | DC single phased
|  | Bit 8 | Cooling fan 1 fault
|  | Bit 9 | Cooling fan 2 fault
|  | Bit 10 | Cooling fan 3 fault
|  | Bit 11 | Cooling fan 4 fault
|  | Bit 12 | Cooling Fan Capacity Fault
|  | Bit 13 | Line unexpected voltage
|  | Bit 14 | Low level comm errors
|  | Bit 15 | DC unbalanced
AL3 | Alarm flags: |  | Read: 1 = alarm active, 0 = alarm inactive. Write: 1 = ack alarm, 0 = no operation.
|  | Bit 0 | Drive output overcurrent
|  | Bit 1 | Simultaneous forward and reverse command
|  | Bit 2 | System boot time exceeded
|  | Bit 3 | System degraded
|  | Bit 4 | Abnormal CPU usage
|  | Bit 5 | Abnormal memory usage
|  | Bit 6 | DC Overvoltage stall prevention
|  | Bit 7 | Motor overcurrent stall prevention
|  | Bit 8 | Line unexpected frequency
|  | Bit 9 | DC Unexpected Frequency
|  | Bit 10 | AFE Fault
|  | Bit 12 | AFE Low voltage ride through
|  | Bit 13 | Remote to local override
|  | Bit 14 | Analog output sensor loss
|  | Bit 15 | PID 1 low process value
AL4 | Alarm flags: |  | Read: 1 = alarm active, 0 = alarm inactive. Write: 1 = ack alarm, 0 = no operation.
|  | Bit 0 | PID 1 high process value
|  | Bit 1 | Control board power loss
|  | Bit 2 | Motor control instability
|  | Bit 3 to 15 | Reserved.
MBPV | MODBUS Profile version:
|  | Bit 0-7 | Minor version
|  | Bit 8-15 | Major version
DIS | Digital Inputs states: |  | Read: 1 = output is high, 0 = output is low
|  | Bit 0 | DI1 - Digital input 1
|  | Bit 1 | DI2 - Digital input 2
|  | Bit 2 | DI3 - Digital input 3
|  | Bit 3 | DI3 - Digital input 4
|  | Bit 4 | DI5 - Digital input 6
|  | Bit 5 to 15 | Reserved.
RELAYS | Relays states: |  | Read: 1 = energized, 0 = not energized
|  | Bit 0 | Relay 1
|  | Bit 1 | Relay 2
|  | Bit 2 | Relay 3
|  | Bit 3 to 15 | Reserved.